## Read me
Severn Trent storm overflow performance pack, 2025 return
Source: Environment Agency EDM annual returns 2024-2025; Met Office HadUK-Grid Midlands rainfall.
Spills counted with the EA 12/24-hour method. River basin derived from WFD waterbody ID.
Sheets: KPIs ¦ By river basin ¦ By asset type ¦ Top catchments ¦ QA checks ¦ QA - large rises ¦ Maintenance exceptions ¦ High-spill exceptions
Context: 2025 Midlands rainfall was 28% below 2024; roughly half the fall in spills is weather (see 02_Findings_Summary.md).

## KPIs
| 2024 | 2025 | Change | Change %
Overflows | 2459 | 2452 | -7 | -0.3
Total spills | 62085 | 36471 | -25614 | -41.3
Total spill hours | 454155 | 200361 | -253794 | -55.9
Avg spills per overflow | 25.4 | 15 | -10.4 | -40.9
Overflows that did not spill | 374 | 429 | 55 | 14.7
Overflows with 60+ spills | 312 | 76 | -236 | -75.6
Monitors working ≥90% of year (%) | 91.3 | 96.3 | 5 | 5.5
Midlands rainfall (mm) | 1000.2 | 716.6 | -283.6 | -28.4

## By river basin
river_basin | Overflows | Spills 2024 | Spills 2025 | Change % | Avg spills/overflow 2025 | Overflows 60+ spills 2025 | Spill hours 2025 | Monitors <90% 2025
Trent (Humber basin) | 1790 | 40738 | 25860 | -36.5 | 14.6 | 58 | 131729 | 63
Severn basin | 635 | 20047 | 9679 | -51.7 | 15.4 | 14 | 61124 | 26
Estuary / other | 27 | 1300 | 932 | -28.3 | 35.8 | 4 | 7509 | 1

## By asset type
asset_type | Overflows | Spills 2024 | Spills 2025 | Change % | Avg spills/overflow 2025 | Overflows 60+ spills 2025 | Spill hours 2025 | Monitors <90% 2025
SO on sewer network | 1396 | 21793 | 15626 | -28.3 | 11.3 | 19 | 36030 | 52
Storm tank at WwTW | 328 | 19632 | 9528 | -51.5 | 29.1 | 30 | 93901 | 10
Storm discharge at pumping station | 564 | 12495 | 7067 | -43.4 | 12.6 | 9 | 41306 | 18
Inlet SO at WwTW | 133 | 5574 | 2953 | -47 | 22.7 | 10 | 15610 | 8
Inlet SO at WwTW - with treatment | 17 | 1433 | 771 | -46.2 | 45.4 | 6 | 7669 | 1
Storm tank at WwTW - with treatment | 14 | 1158 | 526 | -54.6 | 37.6 | 2 | 5846 | 1

## Top catchments
wfd_catchment | Overflows | Spills_2025 | Overflows_60plus
Derwent from Wye to Amber | 34 | 1038 | 6
Trent from Soar to The Beck | 38 | 942 | 4
Amber from Alfreton Brook to Derwent | 27 | 646 | 1
Severn - conf Bele Bk to conf Sundorne Bk | 35 | 615 | 1
Derwent from Bottle Brook to Trent | 30 | 599 | 0
Derwent from Amber to Bottle Brook | 33 | 475 | 0
Severn River and Trib Estuary | 12 | 439 | 3
Tame - conf two arms to R Rea | 45 | 434 | 2
Erewash from Source to Nethergreen Brook | 22 | 431 | 2
Erewash from Gilt Brook to Trent | 26 | 397 | 0
Trent - R Tame to R Dove | 27 | 381 | 1
Derwent from Westend to Wye | 9 | 342 | 2
Bottesford Beck Catchment (trib of Trent) | 19 | 339 | 1
Amber from Source to Press Brook | 5 | 338 | 3
Wye from Monk's Dale to Derwent | 12 | 337 | 1
Stour (Worcs) source to conf Smestow Bk | 42 | 321 | 0
Trent - Ford Green Bk to Fowlea Bk | 24 | 307 | 0
Ouse Dyke Catchment (trib of Trent) | 12 | 296 | 0
Lyme Brook Catchment (trib of Trent) | 28 | 294 | 0
Saredon Brook from Source to River Penk | 24 | 288 | 0

## QA checks
Check | Result | Status | Note
Overflows listed | 2452 | Info
Duplicate overflow IDs | 0 | Pass | Each overflow should appear once
Overflows with no spill count | 21 | Review | Expected only for decommissioned overflows
Monitors working <90% of year | 90 | Review | Reason must be given for each
...of which missing a reason | 0 | Pass | EA requires a reason below 90%
EDM operation above 100% | 0 | Pass | Impossible value
Spill duration above hours in year (8,760) | 0 | Pass | Impossible value
Spills recorded with zero duration | 0 | Pass | Inconsistent pair
New overflows vs 2024 return | 11 | Review | Confirm new or re-referenced assets
Overflows dropped since 2024 return | 18 | Review | Confirm removal / permit revoked
Overflows whose spills rose 50+ in a drier year | 2 | Review | Confirm with operations before publication

## QA - large rises
unique_id | site_name | river_basin | asset_type | spills_2024 | spills_2025 | edm_op_pct
SVT01569 | MILL STREET CSO | Severn basin | Storm discharge at pumping station | 0 | 151 | 99.32
SVT00684 | CROMFORD ROAD - CSO NO 3 | Trent (Humber basin) | SO on sewer network | 4 | 63 | 95.85

## Maintenance exceptions
unique_id | site_name | river_basin | asset_type | edm_op_pct | op_2024 | Repeat (<90% in 2024 too) | low_op_reason
SVT00656 | COVENTRY ROAD STORM OVERFLOW | Trent (Humber basin) | SO on sewer network | 20.48 | 83.95 | TRUE | Access - Unable to retrieve data from non-telemetry data logger
SVT00029 | ADJ. TYSOE STW - STM/EMERG O/F | Severn basin | SO on sewer network | 64.63 | 85.99 | TRUE | Installation set-up/design issue
SVT01871 | RAY HALL COMBINED SEWER OVERFLOW | Trent (Humber basin) | SO on sewer network | 65.85 | 49.97 | TRUE | Sensor failure / issue
SVT02700 | SCREVETON - KNIGHTS CLOSE (CSO) | Trent (Humber basin) | SO on sewer network | 66.19 | 23.84 | TRUE | Sensor failure / issue
SVT01921 | LUTTERWORTH - FOX INN CSO | Severn basin | SO on sewer network | 73.13 | 60.88 | TRUE | Comms failure / issue
SVT01254 | KIDDERMINSTER OLDINGTON STW | Severn basin | Storm tank at WwTW | 73.82 | 89.72 | TRUE | Installation set-up/design issue
SVT02677 | ST MARYS WATER LN ST O/F | Severn basin | SO on sewer network | 76.46 | 82.78 | TRUE | Sensor failure / issue
SVT02591 | WOLVERHAMPTON - BILSTON ROAD 2 CSO | Trent (Humber basin) | SO on sewer network | 76.63 | 45.01 | TRUE | Telemetry or data archiving failure / issue
SVT00891 | FENNY COMPTON STW | Severn basin | Inlet SO at WwTW - with treatment | 79.03 | 56.5 | TRUE | Installation set-up/design issue
SVT00749 | TIPTON - DENBIGH ROAD (CSO) | Trent (Humber basin) | Storm discharge at pumping station | 81.95 | 84.98 | TRUE | Telemetry or data archiving failure / issue
SVT01917 | ROYAL MEADOW DRIVE CSO | Trent (Humber basin) | SO on sewer network | 83.97 | 0 | TRUE | Installation set-up/design issue
SVT01374 | LISTER'S CAR PARK CSO | Severn basin | SO on sewer network | 84.13 | 40.26 | TRUE | Installation set-up/design issue
SVT01120 | HIGH STREET (DOSTHILL) CSO | Trent (Humber basin) | SO on sewer network | 84.42 | 46 | TRUE | Installation set-up/design issue
SVT02467 | WATERHOUSES PUMPING STATION | Trent (Humber basin) | Storm discharge at pumping station | 84.51 | 38.88 | TRUE | Installation set-up/design issue
SVT02287 | THE FLEET COMBINED SEWER OVERFLOW | Trent (Humber basin) | SO on sewer network | 84.66 | 23.32 | TRUE | Installation set-up/design issue
SVT01088 | HAUGHTON SEWAGE TREATMENT WORKS | Trent (Humber basin) | Storm tank at WwTW | 84.79 | 57.51 | TRUE | Comms failure / issue
SVT00277 | GREAT BARR - BISHOPS ASBURY CRES (CSO) | Trent (Humber basin) | SO on sewer network | 86.83 | 44.86 | TRUE | Installation set-up/design issue
SVT01696 | NUTHALL ROAD CSO | Trent (Humber basin) | SO on sewer network | 86.97 | 55.49 | TRUE | Power failure / issue
SVT02571 | WINCHCOMBE SEWAGE TREATMENT WORKS | Severn basin | Storm tank at WwTW | 87.92 | 52.91 | TRUE | Telemetry or data archiving failure / issue
SVT00818 | EAST BRIDGFORD STW | Trent (Humber basin) | Storm tank at WwTW | 87.95 | 44.93 | TRUE | Telemetry or data archiving failure / issue
SVT02299 | THE OVAL SEWAGE PUMPING STATION | Severn basin | Storm discharge at pumping station | 87.96 | 49.79 | TRUE | Telemetry or data archiving failure / issue
SVT02652 | YEAVELEY STW | Trent (Humber basin) | Inlet SO at WwTW | 88.05 | 16.52 | TRUE | Installation set-up/design issue
SVT01352 | LEWIS CLOSE PUMPING STATION | Severn basin | Storm discharge at pumping station | 88.28 | 88.3 | TRUE | Comms failure / issue
SVT01303 | KNOCKIN PUMPING STATION | Severn basin | SO on sewer network | 88.51 | 56.28 | TRUE | Sensor failure / issue
SVT02395 | VARIOUS CSO'S-MELTON MOWBRAY AREA | Trent (Humber basin) | SO on sewer network | 89.07 | 53.94 | TRUE | Capital / maintenance works affect EDM operation
SVT02413 | VICTORIA AVE / CRESCENT LN CSO | Severn basin | SO on sewer network | 89.26 | 83.75 | TRUE | Capital / maintenance works affect EDM operation
SVT01117 | HIGH ROAD SEWAGE PUMPING STATION | Trent (Humber basin) | SO on sewer network | 89.52 | 23.53 | TRUE | Sensor failure / issue
SVT00123 | ASHBY RD/STAPENHILL RD JCN SSO | Trent (Humber basin) | SO on sewer network | 0 | 100 | FALSE | Installation set-up/design issue
SVT02729 | SOUTH NORMANTON STW 6DWF (SO) | Trent (Humber basin) | Inlet SO at WwTW | 7.29 |  | FALSE | Installation set-up/design issue
SVT02722 | STOURPORT ON SEVERN - WORCESTER ROAD (CSO) | Severn basin | SO on sewer network | 7.79 | 96 | FALSE | Installation set-up/design issue
SVT00268 | BIRCH DRIVE CSO | Severn basin | SO on sewer network | 17.43 | 96.01 | FALSE | Installation set-up/design issue
SVT00846 | EDWARD STREET CSO | Trent (Humber basin) | SO on sewer network | 19.73 | 99.99 | FALSE | Installation set-up/design issue
SVT02636 | WORKSOP - MANTON STW | Trent (Humber basin) | Storm tank at WwTW | 32.69 | 99.64 | FALSE | Installation set-up/design issue
SVT02725 | MARKET DRAYTON - WALKMILL RD (CSO) | Severn basin | Storm discharge at pumping station | 34.06 |  | FALSE | Comms failure / issue
SVT01673 | NORTHWOOD PRIME ST-CARDWELL ST CSO | Trent (Humber basin) | SO on sewer network | 34.11 | 99.99 | FALSE | Comms failure / issue
SVT00707 | CSO AT STAPLETON SPS | Trent (Humber basin) | Storm discharge at pumping station | 44.42 | 98.82 | FALSE | Installation set-up/design issue
SVT00299 | BLYTH (NORNAY) PUMPING STATION | Trent (Humber basin) | Storm discharge at pumping station | 56.48 | 91.9 | FALSE | Sensor failure / issue
SVT00449 | CAKEMORE RD COMBINED SEWER OVERFLOW | Trent (Humber basin) | SO on sewer network | 57.81 | 98.35 | FALSE | Installation set-up/design issue
SVT01844 | QUEENS MEAD PMP ST EMG O/F & SUR WT | Severn basin | Storm discharge at pumping station | 61.12 | 90.55 | FALSE | Sensor failure / issue
SVT00428 | BURTON LAZARS SEWAGE TREATMENT WORK | Trent (Humber basin) | Inlet SO at WwTW | 63.5 | 99.95 | FALSE | Sensor failure / issue
SVT00791 | DRAYCOTT SPS - EMERGENCY OVERFLOW | Trent (Humber basin) | Storm discharge at pumping station | 64.79 | 99.98 | FALSE | Installation set-up/design issue
SVT02705 | CROMFORD - DERBY RD (BUS SHELTER) (CSO) | Trent (Humber basin) | SO on sewer network | 65.17 |  | FALSE | Telemetry or data archiving failure / issue
SVT00896 | FERRY ST/FREDERICK ST JUNCTION CSO | Trent (Humber basin) | SO on sewer network | 66.73 | 95.75 | FALSE | Installation set-up/design issue
SVT00168 | BALSALL HEATH - MARY STREET CSO | Trent (Humber basin) | SO on sewer network | 70.88 | 100 | FALSE | Comms failure / issue
SVT00970 | WICKHAMFORD - GOLDEN LANE SPS | Severn basin | Storm discharge at pumping station | 74.71 | 96.99 | FALSE | Power failure / issue
SVT01373 | LIONEL STREET CSO | Trent (Humber basin) | SO on sewer network | 75.24 | 96.06 | FALSE | Sensor failure / issue
SVT01630 | NEWBOROUGH SEWAGE TREATMENT WORKS | Trent (Humber basin) | Inlet SO at WwTW | 77.58 | 99.95 | FALSE | Installation set-up/design issue
SVT00761 | DERRINGTON SEWAGE TREATMENT WORKS | Trent (Humber basin) | Inlet SO at WwTW | 77.71 | 99.95 | FALSE | Installation set-up/design issue
SVT01015 | GRINDLEFORD SEWAGE P S | Trent (Humber basin) | Storm discharge at pumping station | 77.9 | 99.99 | FALSE | Sensor failure / issue
SVT01398 | NECHELLS - LONG ACRE/HOLBORN HILL (CSO) | Trent (Humber basin) | SO on sewer network | 78.08 | 100 | FALSE | Telemetry or data archiving failure / issue
SVT01893 | RIPLEY SEWAGE TREATMENT WORKS | Trent (Humber basin) | Storm tank at WwTW | 78.98 | 100 | FALSE | Sensor failure / issue
SVT01273 | YARDLEY WOOD ROAD CSO | Trent (Humber basin) | SO on sewer network | 81.4 | 100 | FALSE | Installation set-up/design issue
SVT01350 | LENTON BOULEVARD - SHERWIN ROAD CSO | Trent (Humber basin) | SO on sewer network | 82.15 | 99.66 | FALSE | Comms failure / issue
SVT00494 | CASTLE ROAD CSO | Severn basin | SO on sewer network | 82.31 | 97.57 | FALSE | Comms failure / issue
SVT01053 | HARBORNE - HIGH STREET/STATION ROAD (CSO) | Trent (Humber basin) | SO on sewer network | 82.73 | 99.86 | FALSE | Comms failure / issue
SVT00985 | GRAVELLY HILL -OFF WALKER DRIVE CSO | Trent (Humber basin) | SO on sewer network | 82.76 | 99.91 | FALSE | Comms failure / issue
SVT00606 | COLE VALLEY EASTERN SEWER | Trent (Humber basin) | SO on sewer network | 82.89 | 97.19 | FALSE | Sensor failure / issue
SVT00592 | COALVILLE - JACKSON STREET (CSO) | Trent (Humber basin) | SO on sewer network | 83.42 | 100 | FALSE | Sensor failure / issue
SVT00811 | DURSLEY - STATION ROAD (CSO) | Severn basin | SO on sewer network | 84.72 | 99.98 | FALSE | Installation set-up/design issue
SVT01191 | HULLAND WARD STW | Trent (Humber basin) | Storm tank at WwTW | 85.78 | 99.76 | FALSE | Comms failure / issue
SVT01106 | HEATH HAYES - BOSTON CLOSE (CSO) | Trent (Humber basin) | SO on sewer network | 86.1 | 99.76 | FALSE | Sensor failure / issue
SVT00234 | BEESTON (LILAC GROVE) STW | Trent (Humber basin) | Storm tank at WwTW | 86.35 | 94.33 | FALSE | Installation set-up/design issue
SVT01024 | HALFORDS LANE/BRASSHOUSE LANE CSO | Trent (Humber basin) | SO on sewer network | 86.85 | 100 | FALSE | Comms failure / issue
SVT02726 | MELBOURNE STW (CSO) | Trent (Humber basin) | Inlet SO at WwTW | 86.85 |  | FALSE | Capital / maintenance works affect EDM operation
SVT02084 | SNEYD LANE CSO | Trent (Humber basin) | SO on sewer network | 87.43 | 100 | FALSE | Comms failure / issue
SVT00545 | CHURCH LANE PUMPING STATION | Trent (Humber basin) | Storm discharge at pumping station | 87.52 | 100 | FALSE | Telemetry or data archiving failure / issue
SVT01955 | SHREWSBURY - SCOTT STREET (CSO) | Severn basin | SO on sewer network | 87.58 | 100 | FALSE | Comms failure / issue
SVT00232 | BEELEY (SSO) | Trent (Humber basin) | Storm discharge at pumping station | 87.65 | 99.97 | FALSE | Installation set-up/design issue
SVT00685 | CROPTHORNE - MAIN STREET SPS | Severn basin | Storm discharge at pumping station | 87.88 | 93.9 | FALSE | Telemetry or data archiving failure / issue
SVT01501 | MARKET OVERTON STW | Trent (Humber basin) | Storm tank at WwTW | 87.93 | 98.38 | FALSE | Installation set-up/design issue
SVT01425 | CALLOW END - LOWER FERRY LANE (CSO) | Severn basin | SO on sewer network | 87.94 | 95.03 | FALSE | Telemetry or data archiving failure / issue
SVT01771 | PEBBLE CLOSE CSO | Severn basin | SO on sewer network | 88.02 | 99.99 | FALSE | Capital / maintenance works affect EDM operation
SVT02465 | WATER STREET CSO | Trent (Humber basin) | SO on sewer network | 88.25 | 99.77 | FALSE | Comms failure / issue
SVT02224 | STOUR VALE ROAD CSO | Severn basin | SO on sewer network | 88.68 | 99.93 | FALSE | Comms failure / issue
SVT02277 | TEMESIDE PUMPING STATION | Severn basin | Storm discharge at pumping station | 88.83 | 99.99 | FALSE | Telemetry or data archiving failure / issue
SVT01651 | NEWTONS LANE JUNCTION CSO | Trent (Humber basin) | SO on sewer network | 88.92 | 99.91 | FALSE | Capital / maintenance works affect EDM operation
SVT01791 | PERSHORE MILL - PERSHORE ROAD CSO | Trent (Humber basin) | SO on sewer network | 88.92 | 100 | FALSE | Comms failure / issue
SVT01141 | HILTON PARK SEWAGE PUMPING STATION | Trent (Humber basin) | Storm discharge at pumping station | 88.96 | 99.38 | FALSE | Installation set-up/design issue
SVT00468 | CANNOCK ROAD CSO | Trent (Humber basin) | SO on sewer network | 89 | 99.96 | FALSE | Sensor failure / issue
SVT00368 | BROADWAY ROAD CSO | Severn basin | SO on sewer network | 89.19 | 99.99 | FALSE | Sensor failure / issue
SVT02590 | WOLVERHAMPTON - BILSTON ROAD 2 CSO | Trent (Humber basin) | SO on sewer network | 89.23 | 100 | FALSE | Sensor failure / issue
SVT01977 | SELLY OAK MOOR GREEN LANE CSO | Trent (Humber basin) | SO on sewer network | 89.3 | 93.12 | FALSE | Sensor failure / issue
SVT00336 | BREEDON ON THE HILL STW | Trent (Humber basin) | Storm tank at WwTW - with treatment | 89.61 | 99.39 | FALSE | Sensor failure / issue
SVT02032 | SHREWSBURY - COLEHAM HEAD (CSO) | Severn basin | SO on sewer network | 89.65 | 92.04 | FALSE | Sensor failure / issue
SVT02436 | WALTHAM ON THE WOLD STW & SPS | Trent (Humber basin) | Storm discharge at pumping station | 89.67 | 98.85 | FALSE | Sensor failure / issue
SVT01447 | LYDNEY SEWAGE TREATMENT WORKS | Estuary / other | Storm tank at WwTW | 89.72 | 94.52 | FALSE | Installation set-up/design issue
SVT02047 | SILVER COURT GARDENS CSO | Trent (Humber basin) | SO on sewer network | 89.75 | 95.96 | FALSE | Comms failure / issue

## High-spill exceptions
unique_id | site_name | receiving_water | river_basin | asset_type | spills_2025 | spills_2024 | hours_2025 | edm_op_pct | No improvement action 2025 | improvement_activity | investigation_activity
SVT00291 | BLAKENEY STW (SSTO) | RIVER SEVERN | Estuary / other | Storm tank at WwTW | 153 | 197 | 1579.3689 | 99.97 | TRUE | No improvement action in reporting period | UWWTR investigation completed, Operational investigation completed
SVT00365 | BROADOAK SEWAGE TREATMENT WORKS | RIVER SEVERN | Estuary / other | Storm tank at WwTW | 87 | 88 | 1127.4017 | 99.81 | TRUE | No improvement action in reporting period | UWWTR investigation completed, Operational investigation completed
SVT00866 | ENDON SEWAGE TREATMENT WORKS | ENDON BROOK | Trent (Humber basin) | Storm tank at WwTW | 83 | 108 | 810.6461 | 99.11 | TRUE | No improvement action in reporting period | UWWTR investigation completed, Operational investigation completed
SVT00289 | BLAKENEY SEWAGE TREATMENT WORKS | RIVER SEVERN | Estuary / other | Inlet SO at WwTW | 77 | 130 | 451.6636 | 99.51 | TRUE | No improvement action in reporting period | UWWTR investigation completed, Operational investigation completed
SVT00778 | DONINGTON-LE-HEATH TOWNSEND LN CSO | RIVER SENCE | Trent (Humber basin) | SO on sewer network | 74 | 135 | 293.9911 | 99.36 | TRUE | No improvement action in reporting period | Env Act (SODRP) investigation ongoing, UWWTR investigation completed, Operational investigation completed
SVT00126 | ASHLEY SEWAGE TREATMENT WORKS | CHATCULL BROOK | Trent (Humber basin) | Inlet SO at WwTW | 71 | 84 | 288.0694 | 99.97 | TRUE | No improvement action in reporting period | Env Act (SODRP) investigation ongoing, UWWTR investigation completed, Operational investigation completed
SVT02635 | WORCESTER STW | RIVER SEVERN | Severn basin | Storm tank at WwTW | 68 | 150 | 975.0419 | 99.99 | TRUE | No improvement action in reporting period | UWWTR investigation completed, Operational investigation completed
SVT01198 | HUTHWAITE SEWAGE TREATMENT WORKS | NUNN BROOK | Trent (Humber basin) | Inlet SO at WwTW | 67 | 87 | 260.6447 | 99.97 | TRUE | No improvement action in reporting period | Env Act (SODRP) investigation ongoing, UWWTR investigation ongoing, Operational investigation completed
SVT02346 | ASTON - TRINITY RD/LODGE RD (CSO) | RIVER TAME | Trent (Humber basin) | SO on sewer network | 66 | 69 | 40.1519 | 99.98 | TRUE | No improvement action in reporting period | Env Act (SODRP) investigation ongoing, UWWTR investigation completed, Operational investigation completed
SVT00684 | CROMFORD ROAD - CSO NO 3 | RIVER EREWASH | Trent (Humber basin) | SO on sewer network | 63 | 4 | 242.9486 | 95.85 | TRUE | No improvement action in reporting period | Env Act (SODRP) investigation ongoing, UWWTR investigation ongoing, Operational investigation completed
SVT01367 | LIME GROVE WALK/BANK ROAD PO CSO | RIVER DERWENT | Trent (Humber basin) | SO on sewer network | 61 | 84 | 33.0717 | 99.97 | TRUE | No improvement action in reporting period | Env Act (SODRP) investigation ongoing, UWWTR investigation completed, Operational investigation completed
SVT01946 | SAREHOLE ROAD 323 CSO | RIVER COLE | Trent (Humber basin) | SO on sewer network | 60 | 74 | 73.6539 | 99.99 | TRUE | No improvement action in reporting period | Env Act (SODRP) investigation ongoing, UWWTR investigation completed, Operational investigation completed
SVT02583 | WITTON ROAD COMBINED SEWER OVERFLOW | RIVER REA | Trent (Humber basin) | SO on sewer network | 60 | 32 | 73.6075 | 99.98 | TRUE | No improvement action in reporting period | Env Act (SODRP) investigation ongoing, UWWTR investigation completed, Operational investigation completed
SVT01447 | LYDNEY SEWAGE TREATMENT WORKS | RIVER SEVERN ESTUARY | Estuary / other | Storm tank at WwTW | 178 | 196 | 1476.1783 | 89.72 | FALSE | Operational improvement completed | UWWTR investigation ongoing, Operational investigation completed
SVT00558 | CHURCH STRETTON STW | TRIB OF QUINNY BROOK | Severn basin | Storm tank at WwTW - with treatment | 162 | 260 | 3256.6233 | 97.53 | FALSE | Operational improvement completed | UWWTR investigation ongoing, Operational investigation completed
SVT02448 | WARSLOW SEWAGE TREATMENT WORKS | WARSLOW BROOK | Trent (Humber basin) | Inlet SO at WwTW - with treatment | 152 | 162 | 2007.4378 | 97.16 | FALSE | Operational improvement completed | Env Act (SODRP) investigation ongoing, UWWTR investigation completed, Operational investigation completed
SVT01569 | MILL STREET CSO | TRIB OF SIDLEYMOOR BROOK | Severn basin | Storm discharge at pumping station | 151 | 0 | 325.0481 | 99.32 | FALSE | Operational improvement completed | Operational investigation completed
SVT02283 | THE CRESCENT CSO | BRADWELL BROOK | Trent (Humber basin) | SO on sewer network | 127 | 97 | 1394.265 | 99.96 | FALSE | Operational improvement ongoing | UWWTR investigation completed, Operational investigation completed
SVT02251 | SUTTON ON TRENT (CROMWELL) WWTW | RIVER TRENT | Trent (Humber basin) | Storm tank at WwTW | 125 | 237 | 1600.7958 | 99.04 | FALSE | Operational improvement completed | UWWTR investigation ongoing, Operational investigation completed
SVT02076 | SNARESTONE SEWAGE TREATMENT WORKS | RIVER MEASE | Trent (Humber basin) | Storm tank at WwTW | 121 | 208 | 1968.6092 | 99.99 | FALSE | UWWTR improvement ongoing, Operational improvement completed | UWWTR investigation completed, Operational investigation completed
SVT01511 | MATLOCK BATH - DALE ROAD (COAL ME- | RIVER DERWENT | Trent (Humber basin) | SO on sewer network | 118 | 109 | 976.9306 | 99.95 | FALSE | Operational improvement ongoing | UWWTR investigation completed, Operational investigation completed
SVT00150 | AVENING SEWAGE TREATMENT WORKS | NAILSWORTH STREAM | Severn basin | Inlet SO at WwTW | 113 | 154 | 759.2131 | 99.98 | FALSE | Operational improvement completed | UWWTR investigation completed, Operational investigation completed
SVT00130 | ASHOVER STW | RIVER AMBER | Trent (Humber basin) | Inlet SO at WwTW | 103 | 148 | 910.8831 | 99.93 | FALSE | Operational improvement completed | UWWTR investigation ongoing, Operational investigation completed
SVT00267 | BINGHAM ROAD CSO | TRIB OF RIVER TRENT | Trent (Humber basin) | SO on sewer network | 95 | 103 | 337.4547 | 99.97 | FALSE | Operational improvement completed | Env Act (SODRP) investigation ongoing, UWWTR investigation ongoing, Operational investigation completed
SVT00538 | CHIPPERFIELD ROAD CSO | A TRIB OF RIVER TAME | Trent (Humber basin) | SO on sewer network | 90 | 95 | 352.7767 | 94.66 | FALSE | Operational improvement completed | Env Act (SODRP) investigation ongoing, UWWTR investigation completed, Operational investigation completed
SVT00234 | BEESTON (LILAC GROVE) STW | PASTURE LANE DYKE | Trent (Humber basin) | Storm tank at WwTW | 88 | 65 | 698.8289 | 86.35 | FALSE | Operational improvement ongoing | UWWTR investigation ongoing, Operational investigation completed
SVT01453 | MADRESFIELD (WATERLOO CLOSE) STW | MADRESFIELD BROOK | Severn basin | Inlet SO at WwTW | 88 | 114 | 1094.1589 | 99.51 | FALSE | Operational improvement completed | UWWTR investigation ongoing, Operational investigation completed
SVT02487 | WELLESBOURNE SEWAGE TREATMENT WORKS | RIVER DENE | Severn basin | Storm tank at WwTW | 87 | 224 | 1509.2606 | 99.98 | FALSE | UWWTR improvement ongoing, Operational improvement completed | UWWTR investigation ongoing, Operational investigation completed
SVT00196 | BASLOW STW | RIVER DERWENT | Trent (Humber basin) | Storm tank at WwTW | 86 | 116 | 915.2308 | 99.99 | FALSE | Operational improvement ongoing | UWWTR investigation ongoing, Operational investigation completed
SVT00740 | DARLEY DALE NO 11 CSO | RIVER DERWENT | Trent (Humber basin) | Storm discharge at pumping station | 84 | 91 | 803.6358 | 99.94 | FALSE | Operational improvement completed | UWWTR investigation ongoing, Operational investigation completed
SVT01302 | KNIVETON STW | KNIVETON BROOK | Trent (Humber basin) | Storm tank at WwTW | 84 | 94 | 995.1222 | 99.62 | FALSE | Operational improvement ongoing | UWWTR investigation completed, Operational investigation completed
SVT01669 | NORTHEND STW | TRIBUTARY OF RIVER DENE | Severn basin | Inlet SO at WwTW - with treatment | 84 | 203 | 287.7406 | 98.3 | FALSE | Operational improvement completed | UWWTR investigation ongoing, Operational investigation completed
SVT00925 | FRANKTON SEWAGE TREATMENT WORKS | TRIBUTARY OF RIVER LEAM | Severn basin | Storm tank at WwTW | 83 | 217 | 1191.3703 | 98.69 | FALSE | Operational improvement completed | UWWTR investigation ongoing, Operational investigation completed
SVT00621 | COLWALL SEWAGE TREATMENT WORKS | CRADLEY BROOK | Severn basin | Storm tank at WwTW | 81 | 143 | 798.7494 | 99.79 | FALSE | Operational improvement completed | UWWTR investigation completed, Operational investigation completed
SVT01710 | OGSTON WTW CSO | RIVER AMBER | Trent (Humber basin) | SO on sewer network | 80 | 79 | 986.2683 | 99.93 | FALSE | Operational improvement completed | UWWTR investigation completed, Operational investigation completed
SVT00166 | BALSALL COMMON WWTW | TRIBUTARY OF RIVER BLYTHE | Trent (Humber basin) | Inlet SO at WwTW - with treatment | 77 | 45 | 1129.4139 | 99.4 | FALSE | UWWTR improvement ongoing, Operational improvement completed | Env Act (SODRP) investigation ongoing, UWWTR investigation completed, Operational investigation completed
SVT01515 | MATLOCK LEA STW | RIVER DERWENT | Trent (Humber basin) | Storm tank at WwTW | 77 | 123 | 1281.5528 | 99.99 | FALSE | Operational improvement completed | Env Act (SODRP) investigation ongoing, UWWTR investigation ongoing, Operational investigation completed
SVT02318 | TICKHILL SEWAGE TREATMENT WORKS | SLUTWELL STREAM | Trent (Humber basin) | Storm tank at WwTW | 77 | 79 | 301.0997 | 99.8 | FALSE | Operational improvement completed | UWWTR investigation ongoing, Operational investigation completed
SVT01573 | MILTON SEWAGE TREATMENT WORKS | RIVER TRENT | Trent (Humber basin) | Storm tank at WwTW | 76 | 147 | 805.9839 | 99.99 | FALSE | Operational improvement completed | UWWTR investigation completed, Operational investigation completed
SVT01154 | HODSOCK WASTEWATER TREATMENT WORKS | TRIBUTARY OF CARLTON BECK | Trent (Humber basin) | Storm tank at WwTW | 75 | 116 | 1018.2683 | 99.31 | FALSE | UWWTR improvement ongoing, Operational improvement completed | UWWTR investigation completed, Operational investigation completed
SVT01242 | KELSTEDGE SEWAGE TREATMENT WORKS | RIVER AMBER | Trent (Humber basin) | Inlet SO at WwTW | 75 | 71 | 207.1758 | 99.3 | FALSE | Operational improvement completed | UWWTR investigation completed, Operational investigation completed
SVT00325 | BRAILSFORD SEWAGE TREATMENT WORKS | TRIBUTARY OF BRAILSFORD BROOK | Trent (Humber basin) | Inlet SO at WwTW - with treatment | 74 | 138 | 569.6553 | 97.33 | FALSE | Operational improvement completed | Env Act (SODRP) investigation ongoing, UWWTR investigation completed, Operational investigation completed
SVT00933 | FROGHALL SEWAGE TREATMENT WORKS | RIVER CHURNET | Trent (Humber basin) | Storm tank at WwTW | 74 | 85 | 1251.6753 | 99.96 | FALSE | Operational improvement completed | UWWTR investigation completed, Operational investigation completed
SVT02577 | WIRKSWORTH SEWAGE TREATMENT WORKS | RIVER ECCLESBOURNE | Trent (Humber basin) | Storm tank at WwTW | 74 | 74 | 1121.1531 | 99.71 | FALSE | Operational improvement ongoing | Env Act (SODRP) investigation ongoing, UWWTR investigation ongoing, Operational investigation completed
SVT01567 | MILL LANE SPS | RIVER STOUR | Severn basin | Storm discharge at pumping station | 73 | 95 | 113.5158 | 99.98 | FALSE | Operational improvement completed | UWWTR investigation completed, Operational investigation completed
SVT02081 | SNEINTON DALE/WATSON ST CSO | RIVER TRENT VIA BECKVALLEY CUL | Trent (Humber basin) | SO on sewer network | 73 | 82 | 122.4419 | 99.95 | FALSE | Operational improvement completed | Env Act (SODRP) investigation ongoing, UWWTR investigation ongoing, Operational investigation completed
SVT00537 | CHILCOTE RBC SEWAGE TREATMENT WORKS | CHILCOTE BROOK | Trent (Humber basin) | Storm tank at WwTW | 72 | 80 | 132.9769 | 97.31 | FALSE | Operational improvement completed | Env Act (SODRP) investigation ongoing, UWWTR investigation completed, Operational investigation completed
SVT00323 | BRADWELL SEWAGE TREATMENT WORKS | BRADWELL BROOK | Trent (Humber basin) | Storm tank at WwTW | 71 | 87 | 1108.8556 | 99.95 | FALSE | Operational improvement completed | UWWTR investigation completed, Operational investigation completed
SVT00722 | DALE ROAD NORTH CSO | RIVER DERWENT | Trent (Humber basin) | SO on sewer network | 71 | 76 | 314.7497 | 99.6 | FALSE | Operational improvement completed | UWWTR investigation completed, Operational investigation completed
SVT01037 | HANBURY STW | TRIBUTARY OF SEELEY BROOK | Severn basin | Inlet SO at WwTW - with treatment | 71 | 89 | 1232.45 | 99.8 | FALSE | Operational improvement completed | Env Act (SODRP) investigation ongoing, UWWTR investigation completed, Operational investigation completed
SVT00891 | FENNY COMPTON STW | TRIBUTARY OF THE RIVER ITCHEN | Severn basin | Inlet SO at WwTW - with treatment | 70 | 250 | 866.0639 | 79.03 | FALSE | Operational improvement completed | UWWTR investigation completed, Operational investigation completed
SVT00994 | GREAT GLEN SEWAGE TREATMENT WORKS | BURTON BROOK | Trent (Humber basin) | Storm tank at WwTW | 69 | 21 | 1184.4981 | 90.79 | FALSE | Operational improvement completed | UWWTR investigation completed, Operational investigation completed
SVT01649 | NEWTON SOLNEY (EAST) SPS | RIVER TRENT (NON-TIDAL) | Trent (Humber basin) | Storm discharge at pumping station | 69 | 134 | 636.9503 | 95.59 | FALSE | Operational improvement completed | Env Act (SODRP) investigation ongoing, UWWTR investigation completed, Operational investigation completed
SVT01791 | PERSHORE MILL - PERSHORE ROAD CSO | RIVER REA | Trent (Humber basin) | SO on sewer network | 69 | 90 | 196.6878 | 88.92 | FALSE | Operational improvement completed | Env Act (SODRP) investigation ongoing, UWWTR investigation completed, Operational investigation completed
SVT02324 | TIDESWELL STW | TIDESWELL BROOK | Trent (Humber basin) | Storm tank at WwTW | 68 | 92 | 772.3956 | 99.9 | FALSE | Operational improvement completed | Env Act (SODRP) investigation ongoing, UWWTR investigation ongoing, Operational investigation completed
SVT02504 | WESSINGTON PUMPING STATION | RIVER AMBER | Trent (Humber basin) | Storm discharge at pumping station | 68 | 102 | 1210.9886 | 99.97 | FALSE | Operational improvement completed | UWWTR investigation completed, Operational investigation completed
SVT01667 | NORTH WARREN ROAD PUMPING STATION | RIVER TRENT | Trent (Humber basin) | Storm discharge at pumping station | 67 | 65 | 378.4983 | 99.93 | FALSE | Operational improvement ongoing | UWWTR investigation ongoing, Operational investigation completed
SVT01797 | PINXTON SEWAGE TREATMENT WORKS | RIVER EREWASH | Trent (Humber basin) | Storm tank at WwTW | 67 | 103 | 1021.5889 | 99.7 | FALSE | Operational improvement completed | Env Act (SODRP) investigation ongoing, UWWTR investigation completed, Operational investigation completed
SVT01888 | RIDGE LANE MANCETTER STW | TRIBUTARY OF BOURNE BROOK | Trent (Humber basin) | Inlet SO at WwTW | 67 | 108 | 636.8425 | 99.97 | FALSE | Operational improvement completed | UWWTR investigation completed, Operational investigation completed
SVT02301 | THE RAILWAY LINE CSO | RIVER DERWENT | Trent (Humber basin) | SO on sewer network | 67 | 64 | 337.6533 | 99.91 | FALSE | Operational improvement completed | Env Act (SODRP) investigation ongoing, UWWTR investigation ongoing, Operational investigation completed
SVT00934 | FROGHALL SEWAGE TREATMENT WORKS | RIVER CHURNET | Trent (Humber basin) | Inlet SO at WwTW | 66 | 79 | 212.4325 | 99.97 | FALSE | Operational improvement ongoing | UWWTR investigation completed, Operational investigation completed
SVT02077 | SNARROWS STW | GRACE DIEU BROOK | Trent (Humber basin) | Storm tank at WwTW | 66 | 104 | 795.5578 | 98.6 | FALSE | UWWTR improvement completed | Env Act (SODRP) investigation ongoing, UWWTR investigation ongoing, Operational investigation completed
SVT01351 | LETWELL SEWAGE TREATMENT WORKS | TRIBUTARY OF CARLTON BECK | Trent (Humber basin) | Storm tank at WwTW | 65 | 100 | 1184.3772 | 98.99 | FALSE | Operational improvement completed | UWWTR investigation ongoing, Operational investigation completed
SVT01690 | NOTTINGHAM ROAD HUCKNALL CSO | TRIBUTARY OF RIVER LEEN | Trent (Humber basin) | SO on sewer network | 64 | 67 | 200.7503 | 99.98 | FALSE | Operational improvement completed | UWWTR investigation completed, Operational investigation completed
SVT00700 | CSO @ DARLEY BRIDGE PUMPING STATION | RIVER DERWENT | Trent (Humber basin) | Storm discharge at pumping station | 63 | 48 | 299.4153 | 99.99 | FALSE | Operational improvement ongoing | UWWTR investigation completed, Operational investigation completed
SVT01288 | KIRK LANGLEY STW | FLAGSHAW BROOK | Trent (Humber basin) | Storm tank at WwTW - with treatment | 63 | 80 | 656.8222 | 98.81 | FALSE | Operational improvement completed | Env Act (SODRP) investigation ongoing, UWWTR investigation completed, Operational investigation completed
SVT01750 | PADLEY HALL CSO | THE HARTSHAY BROOK | Trent (Humber basin) | SO on sewer network | 63 | 42 | 215.6722 | 99.99 | FALSE | Operational improvement ongoing | Env Act (SODRP) investigation ongoing, UWWTR investigation ongoing, Operational investigation completed
SVT00304 | BOMERE HEATH STW | LEATON BROOK | Severn basin | Storm tank at WwTW | 62 | 72 | 998.2633 | 99.98 | FALSE | Operational improvement completed | UWWTR investigation ongoing, Operational investigation completed
SVT00345 | BRIDGE STREET PUMPING STATION SSO | RIVER TRENT | Trent (Humber basin) | Storm discharge at pumping station | 62 | 67 | 40.3853 | 99.99 | FALSE | Operational improvement completed | UWWTR investigation completed, Operational investigation completed
SVT00821 | EAST COMMON LANE CSO | TRIBUTARY OF BOTTESFORD BECK | Trent (Humber basin) | SO on sewer network | 61 | 76 | 231.2644 | 99.83 | FALSE | UWWTR improvement completed, Operational improvement completed | Env Act (SODRP) investigation ongoing, UWWTR investigation ongoing, Operational investigation completed
SVT01157 | HOGNASTON SEWAGE TREATMENT WORKS | HENMORE BROOK | Trent (Humber basin) | Inlet SO at WwTW | 61 | 102 | 667.0728 | 94.4 | FALSE | Operational improvement completed | UWWTR investigation completed, Operational investigation completed
SVT01339 | LEEK - JUNCTION ROAD CSO | TRIBUTARY OF RIVER CHURNET | Trent (Humber basin) | SO on sewer network | 61 | 69 | 142.4803 | 99.95 | FALSE | Operational improvement ongoing | UWWTR investigation completed, Operational investigation completed
SVT01432 | LOWER LODE LANE PUMPING STATION | MILL AVON | Severn basin | Storm discharge at pumping station | 61 | 110 | 550.7358 | 99.99 | FALSE | Operational improvement completed | UWWTR investigation completed, Operational investigation completed
SVT02528 | WESTWOOD BROOK STW | MORTON BROOK | Trent (Humber basin) | Storm tank at WwTW | 61 | 120 | 529.1158 | 99.98 | FALSE | Operational improvement completed | Env Act (SODRP) investigation ongoing, UWWTR investigation ongoing, Operational investigation completed
SVT00446 | BUXTON WASTEWATER TREATMENT WORKS | RIVER WYE | Trent (Humber basin) | Storm tank at WwTW | 60 | 67 | 612.4647 | 99.39 | FALSE | Operational improvement ongoing | Env Act (SODRP) investigation ongoing, UWWTR investigation completed, Operational investigation completed
SVT00570 | CLAY CROSS SEWAGE TREATMENT WORKS | SMITHY BROOK | Trent (Humber basin) | Storm tank at WwTW | 60 | 72 | 569.0444 | 99.85 | FALSE | Operational improvement completed | UWWTR investigation completed, Operational investigation completed